City of Coquitlam – Anhydrous Ammonia

Exposure Control Plan

Prepared By:

City of Coquitlam

Human Resources

3000 Guildford Way

Coquitlam, BC

V3B 7N2

December, 2013

TABLE OF CONTENTS

Page

Definitions……........………………………..………………………………….………..…………………………..1

Scope…………………………...……………………………………………….……….………….……………….2

Health and Safety Statement & Purpose……………………………………………..…………………………..2

Responsibilities.......…………………………………………………………………….…………………………..2

Risk Identification & Assessment …………………………………………………….…………………………..3

1.0	Ammonia Properties / Hazards	7

1.1	Ammonia – What is it?	7

1.2	Exposure Limits and Health Effects	7

2.0	Education & Training	8

2.1	Workplace Hazardous Materials Information System (WHMIS)	8

2.2	Qualified Personnel Training	8

2.3	Resources	8

3.0	ICE REFRIGERATION system/ammonia plant	9

3.1	Ammonia Storage	9

3.2	Ammonia Alarms	9

3.3	Alarm Response	9

3.4	Working Alone	10

4.0	personal protective equipment	10

4.1	Respirator	10

4.2	Hand / Foot / Body Protection	10

4.3	Eye Protection	11

5.0	First Aid & Health monitoring	11

5.1	Inhalation Treatment	11

5.2	Eye Contact Treatment	11

5.3	Skin Contact Treatment	11

5.4	Health Monitoring	11

6.0	Emergency response	12

6.1	Emergency Contact List	12

6.2	Emergency Equipment and First Aid Kits	12

6.3	Ammonia Leak Emergency	12

6.4	Evacuation Procedure	12

6.5	Evacuation Roles & Responsibilities	13

7.0	Record Keeping & Investigation	15

7.1	Record Keeping	15

7.2	Investigation & Reporting	15

8.0	written work procedures	16

8.1 Safe Work Procedure - Ammonia Plant Entry	17

8.2 Safe Work Procedure- Draining Ammonia Plant Oil Pots	18

8.3 Safe Work Procedure- Alarm / Leak Response & Investigation	19

8.4 Safe Work Procedure- Emergency Plant Shutdown	20

8.5 Safe Work Procedure- Critical Emergency Components of Plant	21

APPENDIX

Ammonia Plant Orientation Checklist

Ammonia Leak Response Flow-chart

Anhydrous Ammonia MSDS (Brenntag March 24, 2011)

Definitions

Anhydrous Ammonia: ammonia gas that has been compressed into a pure liquefied form for use in refrigeration systems.

Cartridge: a filter used in conjunction with a full face respirator that can be used by workers involved in ammonia plant maintenance, or entry when ammonia concentration is  greater than 25ppm and less than 300ppm.

Controlled leak: a release of gas which occurs while maintenance work is being done where the source of the release is immediately known and can be quickly remedied or corrected.

IDLH: immediately dangerous to life and health.

NH3: the chemical formula for ammonia

ppm: parts per million.

PPE: Personal Protective Equipment (boots, gloves, respirator, glasses, etc.)

Qualified personnel: personnel knowledgeable of the work, the hazards involved and the means to control the hazards by reason of education, training, experience or a combination thereof.  See page 5, Section 2.2 for criteria in determining whether a person is qualified.

Uncontrolled leak: a release of gas where the immediate cause of the leak is unknown, or when maintenance work is being done a release of gas occurs of a nature that cannot be quickly remedied, corrected, or controlled.

WHMIS: Workplace Hazardous Materials Information System.

Scope

This Ammonia program forms part of the City of Coquitlam’s Health and Safety Program and complies with the requirements of WorkSafeBC and the Occupational Health and Safety Regulations (OHSR).  This program is specifically designed to be used at the Poirier Sports & Leisure Complex which is the location of the city’s curling and ice rinks:

The purpose of this Program is to satisfy the WCB regulation regarding toxic process gasses (Sections 6.116 – 6.121) and also satisfy the requirements of an exposure control plan detailed in section 5.54 of the WCB regulation.  Compliance with these regulations will enable The City of Coquitlam to protect employees from the potential hazards of working with or around anhydrous ammonia.

Health and Safety Statement & Purpose

The City of Coquitlam is committed to providing a healthy and safe working environment for all of its employees.  To achieve this goal, the City demonstrates a strong commitment to safety by making it a priority in all of the City’s daily operations.

The success of the City’s Health and Safety Program is based on the equal commitment of management and employees.  This can be accomplished through awareness, leadership, cooperation and participation.  To this end, the City strongly supports the Joint Health and Safety Committee and invites input from all employees regarding workplace safety.

Responsibilities

Employer   will review this program on a regular basis and ensure it is implemented and remains compliant.

Supervisors   will ensure all workers are trained, have appropriate personal protective equipment (PPE) and comply with these procedures.

Workers   are responsible to follow all procedures, maintain their PPE and wear it according to procedures.

Risk Identification & Assessment

The following job descriptions have been identified as having risk of exposure to ammonia in excess of 50% of the established exposure limit:

- Arena Maintenance Supervisor

- Arena Maintenance Lead Hand

- Arena Maintenance Worker

- Pool and Building Service Worker

The previously mentioned job descriptions were assessed by the H&S Coordinator and some were found to have moderate and high risk levels.  Controls were administered to mitigate the risks and bring the hazard level down to a low and acceptable level.  Table A (below) represents the summary of a post-control hazard assessment for the job descriptions identified above.  Controls used to mitigate the risks of exposure can be found throughout this document.  These controls include but are not limited to:

- Construction of ammonia plant and sealed shafts containing ammonia lines

- Alarm system that constantly monitors ammonia concentration

- Worker education & training

- Written safe work procedures for ammonia plant tasks

- Emergency facilities and first aid availability

- Use of personal protective equipment

- Emergency response & evacuation procedures

- Incident Investigation and Exposure Control Plan review

Table A

1=lowest, 8=highest

| Job Description | Hazard Scores (1-8) | Risk Level |
| --- | --- | --- |
|  | Probability of an incident | Frequency of Exposure | Severity |  |
| Arena Maintenance Supervisor | 3 | 5 | 3 | (45) Low |
| Arena Maintenance Lead Hand | 3 | 6 | 3 | (54) Low |
| Arena Maintenance Worker | 3 | 6 | 3 | (54) Low |
| Pool and Building Service Worker | 1 | 2 | 3 | (6) Low |

## Ammonia Properties / Hazards

## Ammonia – What is it?

Ammonia is a colorless gas made up of Hydrogen and Nitrogen ions (NH3).  It can easily be turned into a liquid through a cooling process or when placed under pressure.

Several characteristics of ammonia include:

- Extremely reactive with strong oxidizers such as chlorine, bromine, iodine, calcium, gold, mercury, silver and hypochlorite bleach.  The mixture would be explosive in nature

- Very irritating to the eyes, nose and other parts of the respiratory tract which makes it easy to detect at low concentrations in the air

- Although ammonia itself has a low fire rating, the presence of oil or other combustibles increases its fire rating.

- Ammonia gas is lighter than air, so it tends to collect in higher areas like ceilings.

- Ammonia is corrosive and can cause chemical burns all over the body.  It also corrodes most alloys, rubbers and plastics

For more information on the characteristics and chemical properties of anhydrous ammonia, refer to its Material Safety Data Sheet (MSDS), in the appendices of this document.

## Exposure Limits and Health Effects

Table 1 - Ammonia Exposure Limits

| Exposure Limit (parts per million) | Description of Exposure Limit |
| --- | --- |
| 25 ppm | Maximum allowable concentration averaged over an 8 hour period |
| 35 ppm | Maximum allowable short-term (15 minutes) exposure limit |
| 300 ppm or more | Immediately dangerous to life and health (IDLH) concentration. The concentration at which a person without appropriate respiratory protection could be fatally injured or could suffer irreversible or incapacitating health effects. |

Table 2 – Toxic Effects of Ammonia

| Ammonia Concentration (parts per million) | Effect |
| --- | --- |
| 2 to 55 ppm | Range of odor threshold * |
| 70 ppm | Stinging or burning of eyes, nose and throat; headache, watering eyes, sneezing, coughing |
| 300 ppm | Severe irritation of eyes, nose and respiratory tract; difficulty breathing, possible burning in lungs (IDLH level) |
| 2000 ppm or more | Can be fatal after a few breaths |

*This does not apply to workers who routinely work with ammonia, as they are often desensitized to the smell of ammonia and are unable to detect it.

# 2.0	Education & Training

## 2.1	Workplace Hazardous Materials Information System (WHMIS)

A WHMIS program ensures that those who work near ammonia are trained in the general hazards of chemicals and know how to obtain the necessary information to safely manage chemicals that they may encounter in the workplace.  A competency test on the topics covered in the WHMIS training is administered to all participants.  Those staff who work directly with the ice refrigeration system are trained to the level of qualified person by completing the training listed below in section 2.2 Qualified Personnel Training.

## 2.2	Qualified Personnel Training

A reference to “qualified personnel” is made throughout this document with regards to City of Coquitlam staff that are permitted to enter the ammonia plant and perform routine maintenance on the ice refrigeration system.  The following job descriptions are considered to be qualified personnel, providing that they have completed the training in the table below:

- Arena Maintenance Supervisor (Class 4 Power Engineers)

- Arena Maintenance Lead Hand ( Class 5 Power Engineers)

- Arena Maintenance Worker (Ice Facility Operator Certificate or 5th Class Power Engineers)

- Employee with Refrigeration Safety Awareness Officer Certification – Limited access and responsibility.  Primary role is to take ammonia plant readings and initiate emergency response procedures if necessary during the period of time when no Class 4 or 5 Power Engineer is on site

|  | Training Topic | Course Length | Frequency | Course Facilitator |
| --- | --- | --- | --- | --- |
| 1 | Ammonia Safety & Handling | 4 hours | Initial & every 3 years | Ammonia Supplier |
| 2 | Respiratory Protection & Fit Testing | 1 hour | Annual | Coordinator, Safety & Training |

Other training may include but is not limited to periodic sessions from equipment suppliers and courses administered by the City of Coquitlam.  Please see the Appendix of this document for a copy of the Ammonia Plant Orientation checklist.

## 2.3	Resources

- Ammonia in Refrigeration Systems, WorkSafeBC, 2006 edition

- Anhydrous Ammonia MSDS, Brenntag, 15 January 2008

- Occupational Health and Safety Regulations

- Supplier Manual (Brenntag Canada, Inc.)

- Gas Detection Controller Operation Manual, Critical Environmental Technologies

# 3.0	ICE REFRIGERATION system/ammonia plant

## 3.1	Ammonia Storage

Three thousand pounds of liquefied ammonia is stored inside the plant in sealed storage tanks.  The refrigeration system is a closed system that continuously uses and reuses the ammonia inside the tanks.  Staff are not required to add or remove ammonia at any time.  Any correction to ammonia levels is not routine and will be performed by either Brenntag, or Cimco personnel.  Key points regarding ammonia storage include:

- Never apply heat to ammonia storage tanks or valves as rupture could occur

- The temperature of storage containers must never reach 50 degrees Celsius.

- Do not store bleach anywhere inside the ammonia plant

- Do not block access to emergency equipment and doors in the storage area

For more information regarding the storage of ammonia, refer to Ammonia in Refrigeration Systems, WorkSafeBC, 2006 edition.

## 3.2	Ammonia Alarms

The following are characteristics of the ammonia alarms located at the Porier Sports & Leisure Complex:

- A visible and digitally displayed alarm located immediately outside of the ammonia plant room activates when the ammonia concentration in the ammonia room reaches 25 ppm (low alarm).    The display flashes and a strobe light is activated

- An audible, visible and digitally displayed alarm activates when the ammonia concentration in the ammonia plant room reaches 300 ppm (high alarm).  Audible alarms can be heard inside and outside of the ammonia plant, while the display located immediately outside of the ammonia plant visually flashes and a strobe light is activated.

- In addition to these on site indicators of an alarm, an emergency email is automatically sent out to the Blackberries of the following people when a high alarm is triggered:

  - Mark Lacroix – City of Coquitlam, Arena Maintenance Supervisor

  - Paul Mercier – CIMCO representative

  - Darcy Hart – IMEC representative

- The alarm systems is calibrated annually (minimum), as outlined in the manufacturer’s instructions

## 3.3	Alarm Response

Only Qualified Personnel are to respond to ammonia alarms.  If a possible ammonia leak is indicated on the ammonia gauge (concentration higher than 1ppm) and the indicated level is below 300 ppm,  qualified personnel are to follow the detailed leak control procedure (Alarm / Leak Response & Investigation) in Section 8.3 of this document (a copy is also placed near the ammonia plant entry door).  If the ammonia concentration on the alarm monitor is above 300 ppm, commence Evacuation Procedures which can be found in the Ammonia Leak Response flow chart in the Appendix of this document, as well as section 6.4(a copy will also be kept beside the ammonia concentration gauge).  If a high alarm or a system shutdown is required, all qualified and affected personnel must be notified.

## 3.4	Working Alone

There must be a check in system to ensure the continued well-being of workers who are working alone or isolated.  Entry of the ammonia room during an alarm state (concentration is between 25ppm –299ppm), or entry to drain the ammonia oil pots is only permitted with a minimum of 2 staff members involved, with one person being a stand by to call for assistance if necessary.  Entry to the ammonia room in a non-alarm state (less than 25ppm) and not for the purpose of draining the oil pots or investigating a leak requires the entrant to inform a co-worker of the estimated duration of the entry and subsequent contact with that co-worker upon exit.

In the event that the co-worker is not contacted within the given time frame, the co-worker will investigate and contact the appropriate emergency response agencies if necessary.

In situations where a co worker is not available, workers must follow the procedures outlined in the City of Coquitlam Working Alone Program.

# personal protective equipment

## 4.1	Respirator

A full face dual canister air purifying respirator is required when ammonia concentrations are between 25ppm – 299ppm.  The full face respirator must be equipped with gas cartridges that protect the worker against ammonia exposure.  The worker must be clean shaven while wearing a respirator and been fit tested within the last year.  Workers shall follow the procedures that they have been trained on regarding respirator use and care.

If the concentration is below 25ppm, workers may enter the plant without donning a respirator.  If the concentration is above 300ppm, workers are not to enter the plant.

## 4.2	Hand / Foot / Body Protection

Due to the corrosive effects of ammonia it is necessary during some tasks to cover up skin that may be exposed. This may include boots, gloves and coveralls.  The individual Safe Work Procedures (Section 8) will outline the protection required for each task.  It is important to note, that clothes must not be contaminated with grease, lubricants or cleaners as they can react violently with ammonia gas causing severe burns.

## 4.3	Eye Protection

When eye protection is required for certain tasks (see Section 8), it will be achieved with the use of the full face respirator.  It is very important that contact lenses are not worn whenever entering or working in the ammonia plant.

# 5.0	First Aid & Health monitoring

Artificial Respiration and CPR are only to be administered by trained personnel.

## Inhalation Treatment

Ensure that the concentration in the ammonia room is below 300ppm and you are wearing your full face respirator.  Move victim to fresh air.  Give artificial respiration ONLY if breathing has stopped.  Give CPR if there is no breathing and no pulse.  Oxygen to be administered by trained personnel.  Obtain medical attention immediately.

## Eye Contact Treatment

If liquid or gaseous ammonia contacts the eyes, the employee needs to be removed from the contaminated area and continuously flush eyes with tempered water for 20 minutes.  The eye wash station is located directly outside of the ammonia room in the pre-entry room.  Ensure that the eyes are held open and there is direct contact between the water and eyes.

## 5.3	Skin Contact Treatment

Liquid ammonia causes the moisture in the skin to freeze (almost instantly with higher concentrations).  Skin should be continually flushed with tempered water.  If a large area has been exposed, do not remove clothing until you have thoroughly rinsed in the emergency shower.  After rinsing, remove any contaminated clothing and obtain medical attention.

## 5.4	Health Monitoring

The WCB and OSHA currently have no requirements for medical surveillance of ammonia exposure. Medical surveillance is intended to protect workers from developing occupational disease by detecting early biological indicators or adverse health effects at an early stage.

The effects of ammonia on humans are largely acute and victims of ammonia exposure in excess of exposure limits will often feel the effects immediately.  Workers who may be exposed to levels of ammonia in excess of exposure limits are trained to seek medical aid following exposures, regardless of route of entry.

# 6.0	Emergency response

## 6.1	Emergency Contact List

A list of emergency contact numbers for qualified ammonia plant entrants, managers and other key personnel will be kept current.  The list will be provided to City of Coquitlam arena staff and the Health & Safety Advisor.  It will be posted in prominent locations as a resource for staff on site.

In an emergency event, the following people must be called immediately:

- Coquitlam Fire Department

- Arena Maintenance Supervisor or Arena Maintenance Lead Hand

- Facility Operations Manager

- Health and Safety Advisor

- Safety Authority

## Emergency Equipment and First Aid Kits

The Poirier Sports & Leisure Complex has an emergency shower and eye wash station inside the pre-entry room.  The shower/eyewash has been plumbed with tempered water to avoid the increased severity of exposures that cold water can cause.

First aid kits are available at several locations in the complex.

## Ammonia Leak Emergency

An ammonia leak is considered an emergency when the concentration in the ammonia plant reaches 300ppm.  As previously stated, the audible alarm will engage when the ammonia concentration reaches 300ppm. Qualified personnel are to be contacted immediately to address the situation.  If the ammonia emergency occurs during non-business hours, follow the same evacuation procedures in section 6.4, but step 2 can be omitted due to the fact that no public are on site and only facility staff need to be evacuated.

## Evacuation Procedure

Evacuation of the facility will commence when qualified personnel have deemed it necessary and or if the fire alarm is triggered.  The building will be evacuated by following the Evacuation Procedures for the Poirier Sports & Leisure Complex (CEDMS#888605).  The following is a summary of the key evacuation steps.

Important Notes:

- DO NOT open the doors leading from the pre-entry room to the skating rink lobby

- DO NOT attempt rescue of any employees / members of the public that are unconscious in ammonia contaminated area. The Coquitlam Fire Department (CFD) will handle this.

Key evacuation steps:

- Call 911, advise that there is an ammonia leak at the facility, provide the address and ask for Coquitlam Fire Department (CFD) to respond.

- (OMIT if outside business hours) Contact the front desk and let them know of the emergency and that an evacuation needs to occur.  Front desk will contact a facility supervisor to lead the evacuation and safely remove all public from the building.

- Call the Facility Operations Manager and provide information on the emergency and the names of the other staff members called.

- The facility supervisor will utilize staff on site to facilitate the building evacuation during business hours ensuring that the following tasks are accomplished:

  - Lifeguard staff clear pools and change rooms, directing public to safe exits

  - Arena staff clear all ice surfaces and change rooms, directing public to safe exits

  - All other public areas are evacuated by designated facility staff

  - Post staff at all public entrances & exits of facility to ensure that patrons do not try and re-enter the building

  - Prevent patrons who have been exposed to high levels of ammonia from leaving without being medically assessed first.

  - All staff not involved in facilitating the evacuation will remove themselves from the building and assemble at the muster station

- During non-business hours, whomever discovers the leak must ensure that any other workers leave the building immediately

- Determine the direction of the wind ASAP and if the muster/marshalling station is downwind of the ammonia room, then a new location upwind of the ammonia room for mustering must be chosen.

- Await arrival of CFD and City management representatives.  Any information about the leak and the site should be passed along to the CFD.

- The CFD will determine when it is safe to allow re-entry into the building.

## 6.5	Evacuation Roles & Responsibilities

Arena Maintenance Supervisor /  Lead Hand Arena Maintenance  /  Arena Maintenance Worker

These are workers who have received formal ammonia training and are primarily responsible for responding to alarms.  At least two qualified and properly trained workers must respond to alarms and perform these roles during an EMERGENCY:

- Respond to alarm and follow procedures for leak investigation.

- When ammonia concentration exceeds 300 ppm, contact Coquitlam Fire Department (CFD), other Emergency Response Agencies (CIMCO, Brenntag) and the front desk receptionist (during business hours).

- Determine direction of wind and whether or not mustering station needs to be moved ( It must be upwind of the ammonia storage room)

- Liaise with CFD and city management reps as they arrive and debrief on situation.  If possible, provide a floor plan of the facility

- Perform any roles that the CFD asks of you and await the decision on re-entry or facility closure.

- The Arena Maintenance worker must attempt to contact the Arena Maintenance Supervisor before ordering an evacuation during times when the general public is in the building

Front Desk Reception

During Business hours, the receptionist at the front desk of the Poirier Sports & Leisure Complex will be contacted by the Arena Maintenance Supervisor/ Worker with the news of a pending evacuation.  The receptionist will then perform the following tasks:

- Contact a Facility Supervisor to coordinate the evacuation

- Call 911 and request the presence of the Coquitlam Fire Department if they haven’t already been called.

- Pull the nearest pull station if the alarm has not yet been deployed.

- Contact the City of Coquitlam staff members on the emergency call list

- Follow the directions of the facility manager coordinating the evacuation

- Evacuate to the Muster Station when tasks are completed

Facilities Supervisor

One of nine Supervisors for the Sports & Leisure Complex that will be called upon to coordinate a full or partial building evacuation during business hours.

Duties include:

- Assignment of building areas to staff for sweeping and evacuation

- Recording of any injured, disabled persons located in stairwells or areas of refuge.

- Ensuring consistent messaging to public both indoors and at the muster station

- Report any missing, or injured/disabled persons to the Coquitlam Fire Department (CFD)

Facility Operations Manager

The Facility Operations Manager will be notified of any facility evacuation and will arrive on site to perform the following roles:

- Ensure that the facility is secure and not permit workers or members of the public to re-enter the facility unless it is deemed safe to do so by the CFD

- Supervise the clean up.

- Arrange assistance and first aid for workers if required.

- Ensure that the incident is reported immediately to the Occupational Health & Safety Advisor and Senior Management.

- Conduct an incident investigation and report findings

- Respond to any media requests

Coquitlam Fire Department (CFD)Role

During the incident, CFD will:

- Respond and upon arrival, the CFD is in charge of the scene and all staff members and managers.  Everyone will report to and follow the directions of the CFD.

- CFD will leave the scene with a responsible person, will not participate in clean up of the incident and will not participate in cleanup of hazardous materials in particular.  If required, hazardous waste clean up contractor should be contacted by the Facility Operations Manager.

# 7.0	Record Keeping & Investigation

## Record Keeping

Proper activity logbooks will be maintained regarding any ammonia issues.  Detailed information will be entered into the logbook for any release large enough to set off the low ammonia alarm (greater than 25 ppm).  Investigations are conducted for any release large enough to set off the high ammonia alarm (greater than 300ppm) and or if an evacuation is performed.  See Section 7.2 for information on ammonia release reporting requirements.  Any outstanding maintenance or supplier issues must be noted in the log book and receive follow up promptly.

## Investigation & Reporting

An ‘incident’ is an accident or other occurrence which resulted in or had the potential for causing an injury or occupational disease.  If enough ammonia is released to set off the high alarm, the City of Coquitlam must conduct an investigation to discover the cause(s) of the incident.  The investigation must also examine measures that will prevent similar incidents in the future.  The City of Coquitlam must forward copies of the investigation report to the Health and Safety Committee.

Note: The City of Coquitlam must immediately notify WorkSafeBC of any major release of a toxic substance.  A major release of ammonia includes:

- A leak or spill resulting in at least one person receiving professional medical attention; or

- A leak or spill resulting in at least three people receiving first aid.

# 8.0	written work procedures

High hazard job tasks require detailed safe work procedures to be developed and made available for staff performing these tasks.  The following tasks have safe work procedures and are found on the following pages:

- 8.1 Ammonia Plant Entry

- 8.2 Draining Ammonia Plant Oil Pots

- 8.3 Alarm / Leak Response & Investigation

- 8.4 Emergency Plant Shut down

## 8.1 Safe Work Procedure - Ammonia Plant Entry

PURPOSE

The purpose of this Safe Work Procedure is to establish a consistent method for entering the Ammonia Plant which is also compliant with all applicable regulations and standards.   Health & Safety of Ammonia Plant entrants is of the utmost importance and is the basis for the following procedure.

This procedure is consistent with the training that is supplied to all entrants of the Ammonia Plant.  Failure to follow these procedures is subject to discipline.

SCOPE

These procedures are applicable to all Ammonia Plant Entrants and are enforceable when the ammonia plant is in operation.  This group includes, but is not limited to the following occupations:

| Arena Maintenance Workers | Electricians | Arena Maintenance Supervisor |
| --- | --- | --- |
| Arena Maintenance Lead hand | Contractors / Inspectors | Health & Safety Coordinator |
| Coquitlam Fire Department |  |

Entry Requirements:  Entrants must possess a Class 4 or 5 Power Engineering Certificate, or a Refrigeration Safety Awareness Officer certificate.  Anyone without this certification must be accompanied by someone with this classification at all times.

PROCEDURES

- Ensure that you satisfy the above entry requirements and are not wearing contact lenses.

- Let your Supervisor, or Co-worker know that you are entering the Ammonia Plant.

- View the ammonia concentration gauge located to the left of the door in the pre-entry room and ensure that its reading is less than 300ppm.  NO ENTRY WHEN LEVELS ARE ABOVE 300ppm.

- Obtain your personal full face respirator.  You must have been fit tested within the last year and have no facial hair where the respirator seals against the skin of your face.  Escape respirators may also be used.

- Respirators are to be carried with you at all times and are to be put on when:

  - Concentration are greater than 25ppm and less than 300ppm

  - An audible / visual alarm is observed while in the Ammonia Plant (after respirator is donned, immediately evacuate the ammonia plant)

  - The task of draining the Oil Pots is undertaken (see Draining Oil Pots SWP for complete details and additional PPE requirements)

  - Minor fluctuations in ammonia concentration are being investigated

  - The strong smell of ammonia is encountered

- Complete your work / plant logs, then inform your Supervisor or co-worker upon plant exit.

**NOTE-  If the audible alarms engage at any point while in the ammonia room, this signifies that the concentration level has reached or surpassed 300 ppm and the plant needs to be evacuated.  Once you have evacuated to the pre-entry room, review the ammonia concentration gauge and perform the required action(s) for the displayed concentration.

| Applicable Regulations: | OHS Regulation: 5.48, 6.119, 5.54, 8.5 |
| --- | --- |
|  | Safety Standards Act M62 |
|  | B52-99 Mechanical Refrigeration Code |

## 8.2 Safe Work Procedure- Draining Ammonia Plant Oil Pots

PURPOSE

The purpose of this Safe Work Procedure is to establish a consistent method for draining the ammonia room oil pots.  When draining the oil pots workers are exposed to levels of ammonia which may exceed 35ppm.  This procedure needs to be followed to ensure that workers are protected from these elevated concentrations of ammonia.

This procedure is consistent with the training that is provided for all entrants to the ammonia plant.  Failure to follow these procedures is subject to discipline.

SCOPE

These procedures are applicable to all Arena Maintenance Workers / Supervisors and Ice Facility Operators (when supervised).

PROCEDURES

- This task requires an additional person to accompany you into the ammonia plant.  This person may place themselves anywhere between you and the exit door but must remain within sight and at a distance where conversation can take place.

- Ensure that you meet the requirements for entry into the Ammonia Plant before entering.

- Obtain an oil pot draining bucket.

- View the ammonia concentration gauge located to the left of the door in the pre-entry room and ensure that its reading is less than 300ppm.  NO ENTRY WHEN LEVELS ARE ABOVE 300ppm.

- Put on your butyl gloves and Full Face respirator.  Perform a positive and negative pressure check to ensure the respirator has made a good seal with your face.

- Once in the ammonia room, let your partner know where you would like him to be.

- Turn off the associated brine pump.

- Remove the Blue Cap to gain access to the release valve on the oil pot.  Use a 5/16” refrigeration wrench to loosen the valve.  Place the draining bucket beneath the valve.

- Use the dead man’s switch / valve on the oil pot to begin releasing the mixture into the bucket.

- Drain the mixture slowly until spitting occurs (this signals that draining is complete) and then release the dead man switch.

- Tighten up the release valve on the oil pot, being careful not to spill any of the mixture.  Allow oil to settle and record the amount of liquid drained.

- After sealing bucket, you may remove Personal Protective Equipment and transport the filled bucket to the storage room accessible from the outside on the North side of the building

**NOTE- If the audible alarm engages at any point while in the ammonia room, this signifies that the concentration level has reached or surpassed 300 ppm and the plant needs to be evacuated.  Once you have evacuated to the pre-entry room, review the ammonia concentration gauge and perform the required action(s) for the displayed concentration.

| Applicable Regulations: | Safety Standards Act M62 |
| --- | --- |
|  | B52-99 Mechanical Refrigeration Code |
|  | OHS Regulation 8.2-8.10, 8.14-8.18, 8.32-8.44 |

## 8.3 Safe Work Procedure- Alarm / Leak Response & Investigation

PURPOSE

The purpose of this Safe Work Procedure is to establish a consistent method for investigating minor leaks in the Ammonia Plant.  The ammonia plant is only to be entered when the levels inside are under 300 ppm, so leak investigation may only be conducted for minor leaks.

This procedure is consistent with the training that is provided for Arena Maintenance staff.  Failure to follow these procedures is subject to discipline.

SCOPE

These procedures are applicable to all Arena Maintenance Workers / Supervisors.

PROCEDURES

- This task requires an additional person to accompany you into the ammonia plant.  This person must have their full face respirator on for the duration of this task and position themselves near the entrance to the ammonia plant with the door open.  This person must maintain visual contact throughout leak investigation and be able to monitor the ammonia concentration gauge.

- Ensure that you and your stand by person meet the requirements for entry into the Ammonia Plant before entering.

- View the ammonia concentration gauge located to the left of the door in the pre-entry room and if the concentration is below 300ppm you may don your full face respirator and enter the ammonia room with the intent of locating the leak.

- Enter the ammonia room and ensure that your partner remains near the open door.

- Begin the investigation by slowly walking around the Ammonia room with the portable ammonia detector in an attempt to identify the general area of the leak.

- Once the general area is identified, return to the pre-entry room and obtain a piece of Litmus paper.

- Return to the general area of the leak. The litmus paper needs to be moistened (do not moisten with your lips), then held at different locations to better pinpoint the location of the leak.

- If the Litmus Paper turns pink, this indicates the presence of Ammonia.  If the leak is found it should be isolated and stopped if possible by shutting valves on either side of the leak and turning the compressors off at the electrical panel.  Contact CIMCO to perform the repairs or if the source of the leak can’t be determined.  If the leak causes the concentration in the ammonia room to reach 300ppm at any time, evacuation procedures must be implemented.

| Applicable Regulations: | OHS Regulation: 5.48, 5.53, 8.5, |
| --- | --- |
|  | Safety Standards Act M62 |
|  | B52-99 Mechanical Refrigeration Code |

## 8.4 Safe Work Procedure- Emergency Plant Shutdown

PURPOSE

The purpose of this Safe Work Procedure is to establish a consistent method for shutting down the ammonia plant in the event of an emergency.  If the concentration is below 300ppm, you may enter the ammonia plant room and physically close the King valve which stops the flow of ammonia through the system.  If the concentration is above 300ppm, then shut down must be performed from the pre-entry room directly outside of the ammonia plant room.

This procedure is consistent with the training that is provided for Arena Maintenance staff.  Failure to follow these procedures is subject to discipline.

PROCEDURES

| Uncontrollable leak under 300ppm | Uncontrollable leak over 300ppm |
| --- | --- |
| Ensure that exhaust fan is on high setting | Close all doors leading to the ammonia plant |
| Entrant & stand by person must be wearing full face respirator | Depress Emergency stop button in pre-entry room and ensure exhaust fan stops |
| Enter ammonia plant and close the King Valve | Commence evacuation procedures |
| Immediately exit plant closing door behind you |  |
| Monitor Plant on DDC terminal in pre-entry room as it will take time for all ammonia to return to the receiver |  |
| If at any point the concentration reaches 300ppm, commence evacuation procedures |  |
| Call CIMCO to respond and repair cause of leak |  |

| Applicable Regulations: | OHS Regulation: 5.48, 5.53, 8.5, |
| --- | --- |
|  | Safety Standards Act M62 |
|  | B52-99 Mechanical Refrigeration Code |

## 8.5 Safe Work Procedure- Critical Emergency Components of Plant

PURPOSE

To identify and explain the functions of two plant components that can be used in an emergency to mitigate risk and assist in controlling the hazards associated with a serious ammonia leak (concentration greater than 300ppm) or fire.

Critical Component #1 – Emergency Remote Shut Off

Location:	Inside the ammonia pre-entry room, to the right of the door leading to the plant at shoulder height.

Description:		2” red, round emergency stop button clearly identified by label

Functions:	When this button is depressed it stops any machinery which is controlled by electrical power.  This will cause the fans to stop running, the compressors will stop (which stops the flow of ammonia through the system) and solenoids will close causing the bulk of the ammonia to remain inside the chillers.

When to be used:	When the concentration in the ammonia room exceeds 300 ppm.  This shut off is used in conjunction with emergency evacuation procedures and the assistance of emergency response teams.

Critical Component #2 – Ammonia Plant Dump Valve

Location:	Accessible via extension ladder from the north parking lot.  The valve is located on the northern most exterior wall of the facility, 12-15 ft high.

Description:		Contained in a red recessed box with a breakable glass front

Functions:	This valve when opened will drain all of the ammonia contained in the receiver.  The ammonia will flow out of a painted red stack on the north side of the roof and disburse into the atmosphere.

When to be used:	This valve is only to be used by the Coquitlam Fire Department in the event of a building fire which has the possibility of entering the ammonia plant and causing a severe explosion.  It is critical that the Fire Department be aware of wind direction prior to using this valve as neighborhood notification of this event must occur.

APPENDIX

TRACKING #  _________

AMMONIA PLANT Orientation CHECKLIST

For Qualified Personnel

| Section A: EMPLOYEE INFORMATION |
| --- |
| Job Title: |
| Employee Name: (Print Clearly) |
| Certification | Refrigeration Safety Awareness Officer Class 4/5 Power Engineer Ice FacilityOperator |
| Supervisor Name: (Print Clearly) |  |
| Section B: MAJOR COMPONENTS – Identify location and explain function in system |
| Evaporator (Chiller) | Receiver |
| Compressor(s) | Expansion Valve |
| Condenser | King Valve |
| Fire Box | Brine Pumps |
| SECTION C: PROCEDURES – The following procedures must be communicated to all entrants |
| Ammonia Plant Entry | Shut Down | Emergency Shut Down |
| Building Evacuation | Logbook Use | Alarm System Use |
| The following procedures must be communicated to Arena Maintenance Workers |
| Draining Ammonia Plant Oil Pots | Alarm / Leak Response & Investigation |

| SECTION D: WORKER & SUPERVISOR ACKNOWLEDGEMENT |
| --- |
|  | Ammonia Plant Entrant Signature | Date |
| I understand and feel comfortable with the material presented to me during this Orientation. |  | ___ / ___ / ___ |
|  | Ammonia Plant Supervisor Signature | Date |
| I have provided the above Orientation and feel comfortable with this worker entering the ammonia plant . |  | ___ / ___ / ___ |

AMMONIA LEAK RESPONSE FLOW CHART

EVACUATION PROCEDURES

# Text boxes

Possible ammonia leak is detected

Is the concentration on the ammonia gauge below 300ppm ?

NO

YES

Press the emergency stop button in the pre-entry room and commence Evacuation Procedures

-See Below-

Only staff with respirator training, an annual fit test and a stand by person may enter the ammonia room.  Both staff must be wearing their full face respirators with appropriate gas cartridges throughout this procedure.

Position stand-by at door to the ammonia plant(inside pre-entry room).  Enter the plant and use the portable ammonia detector to locate the general area of the leak.  Once the area is located, return to pre-entry room.

Contact Arena Maintenance Supervisor, then Coquitlam Fire Department (CFD) (911), to let them know that you have an ammonia leak and give facility address.  If you have not already called CIMCO and or Brenntag, call them now.  CIMCO (604)                  BRENNTAG(604)

Stand-by should watch the entrant and monitor the ammonia gauge ensuring that if it reaches 300ppm, the plant and building are evacuated. (see above left)

Contact the front desk reception, let them know there is an ammonia leak and to commence evacuation of the building.  Inform them if the wind direction has affected the location of the muster station.

(Omit if outside of regular business hours).  Reception will contact a Facility Supervisor to coordinate the evacuation who will in turn:

  - Pull the nearest pull station if not already done

  - Have staff begin sweeping and evacuating public areas

  - Post staff at all public entrances & exits of facility to ensure that patrons do not try and re-enter the building

- Identify areas containing injured/disabled people and communicate to CFD upon arrival

In the pre-entry room, obtain a moistened piece of litmus paper.  Don your respirator and return to the ammonia plant and place the litmus paper at various points in the general area of the leak (the litmus will turn pink when in contact with ammonia gas)

If you are able to identify the source of the leak, isolate it by shutting off any surrounding valves, then shut off the compressors at the electrical panel.  If you are unable to locate, or isolate the leak, immediately call CIMCO.  If the leak is large enough to increase the concentration to 300ppm, an evacuation must occur immediately. (see above left)

Reception will also contact, Facility Operations Manager and H&S Advisor to advise of situation.

Monitor concentration to ensure it doesn’t reach 300ppm and wait for CIMCO to make repairs.

You may continue to look for the leak, using the litmus paper, or you may choose to perform an emergency shut down of the ammonia plant.  If at any point the concentration reaches 300ppm the building must be evacuated immediately

Await arrival of CFD and City Management reps, then provide any requested information.

YES

NO

Has the leak been isolated and the ammonia concentration stopped increasing?

IMPORTANT NOTES:

- DO NOT leave any ammonia plant doors open, or any doors near the ammonia room that lead to public areas

- DO NOT attempt rescue of any employees /guests that are unconscious in a contaminated area

The CFD is responsible for these tasks and to make the decision to dump the contents of the ammonia plant (emergency valve)